## Slide 1
AG3000
Horizontal Installation Overview

## Slide 2
Step 1
You’ll Need:
Measure the horizontal straight pipe from pump.
Ensure there is sufficient straight pipe to meet the requirements of the meter.
AG3000-300 22“ total minimum straight pipe
AG3000-400 22“ total minimum straight pipe
AG3000-600 30" total minimum straight pipe
Tape Measure
Installing an AG3000
Total minimum straight pipe for your meter – see below.
Meter + Flanges
+ Gaskets
+ Grounding rings
AG3000-800 38" total minimum straight pipe
AG3000-1000 48“ total minimum straight pipe
AG3000-1200 60" total minimum straight pipe
2X Pipe Diameter
Upstream
1X Pipe
Diameter
Downstream

## Slide 3
Cut out a section of straight pipe, insuring there are at least two pipe diameters of straight pipe on the inlet side of the meter, and one pipe diameter of straight pipe on the outlet side of the meter.
Tape Measure
Cutting Tools
Installing an AG3000
Step 2
You’ll Need:
This meter is sensitive to heat. Do not weld or flame cut within 10’ of meter. Heat will damage electronics and liner. (Heat damage will void warranty.)
Meter + Flanges
+ Gaskets
+ Grounding rings
2X Min. Pipe Diameter
Upstream
1X Min. Pipe
Diameter
Down

## Slide 4
Cut out a section of straight pipe, ensuring there are at least two pipe diameters of straight pipe upstream of the meter, and one pipe diameter of straight pipe downstream of the meter.
Tape Measure
Cutting Tools
Installing an AG3000
Step 3
You’ll Need:
2X Min. Pipe Diameter
Upstream
1X Min. Pipe
Diameter
Down
This meter is sensitive to heat. Do not weld or flame cut within 10’ of meter. Heat will damage electronics and liner. (Heat damage will void warranty.)
Meter/Flanges/
Gaskets/
Grounding rings

## Slide 5
Weld the appropriate ANSI pattern flanges on each open end of pipe, ensuring the flanges are parallel, and the flange bolt holes are aligned.
Allow the welds to cool to ambient temperature.
Tape Measure
Welding Tools
Level
Installing an AG3000
Step 4
You’ll Need:
This meter is sensitive to heat. Do not weld or flame cut within 10’ of meter. Heat will damage electronics and liner. (Heat damage will void warranty.)

## Slide 6
Weld the appropriate ANSI pattern flanges on each open end of pipe, ensuring the flanges are parallel, and the flange bolt holes are aligned.
Allow the welds to cool to ambient temperature.
Tape Measure
Welding Tools
Level
Installing an AG3000
Step 5
You’ll Need:
WARNINGS:
THE HEAT AND/OR ELECTRICAL
CURRENTS FROM THE WELDER
WILL DAMAGE THE METER
AND VOID THE WARRANTY.
THE PIPE MUST NOT EXTEND
PAST THE SURFACE OF THE
FLANGE
Ensure bolt holes are aligned
This meter is sensitive to heat. Do not weld or flame cut within 10’ of meter. Heat will damage electronics and liner. (Heat damage will void warranty.)

## Slide 7
Flow arrow points downstream
Torque Wrench
Installing an AG3000
FLOW
Step 6
You’ll Need:
Install only with full face gasket on each end of the meter.
Insert the meter, gaskets and grounding rings (if applicable), with the direction arrow on the side of the meter pointed down stream in the direction of the flow.
Although the meter is shown installed in the 12:00 position for visual purposes, which is acceptable, the ideal installation is to rotate the meter one bolt hole to a slightly angled position.

## Slide 8
Bolt the meter to the flanges using the appropriate sequence and torque.
Installing an AG3000
Step 6
You’ll Need:
1
2
3
4
5
8
7
6
AG3000-300 25 ft-lb
AG3000-400 20 ft-lb
AG3000-600 42 ft-lb
AG3000-800 65 ft-lb
AG3000-1000 73 ft-lb
AG3000-1200 97 ft-lb
Torque Wrench

## Slide 9
Install the equalization wires and tabs from the lug to the outside pipe flanges (not in direct contact with the meter) for proper electrical grounding.
Wire Cutters
Tab on pipe flange
NOT
meter flange
Tab on pipe flange
NOT
meter flange
Installing an AG3000
Step 7
You’ll Need:
Torque Wrench
#2 Phillips Screw Driver

## Slide 10
Install the equalization wires and tabs from the lug to the outside pipe flanges (not in direct contact with the meter) for proper electrical grounding.
Wire Cutters
Installing an AG3000
Step 8
You’ll Need:
Ensure proper grounding.
See instruction manual for more information on grounding the meter.
Torque Wrench
#2 Phillips Screw Driver

## Slide 11
If cables from meter to other electronics will be needed in the field, install cables. See manual for specific wiring requirements for your application.
Wrench
Wire Cutters
Installing an AG3000
Step 9
You’ll Need:
Inspect and clean O-ring and threads on plastic wire gland and cap.
#2 Phillips Screw Driver

## Slide 12
If meter does not have a factory installed hinged weather guard, attach the weather guard cover and lanyard.
Installing an AG3000
Step 10
You’ll Need:

## Slide 13
Connect the security seal.
Installing an AG3000
Step 11
You’ll Need:

## Slide 14
Your meter is installed!
Refer to the Seametrics AG3000 Instruction Manual for additional information and programming instructions.
Installing an AG3000
Step 12
You’ll Need:

## Slide 15
For Additional Support Call: 800-975-8153