- General

  - All indicators furnished shall be manufactured by a registered ISO 9001 quality standard facility

  - All indicators are to be manufactured in the USA

  - Indicators supplied shall be from a US based company that has manufactured indicators for at least ten (10) years and who distributes all types and flow transmitters as indicated in these specifications

- Type

  - Indicators shall be of the digital type

- Capacity

  - The capacity of the indicators, in terms of normal operations, shall provide rate, total, and pulse output at a minimum

- Function/Performance

  - Operating Temperature: -32° to 131° F (0° to 55° C)

  - Non-Operating Temperature: -40° to 158° F (-40° to 75° C)

  - Rate Display: 5-digit auto-range, 0.65” (16.5mm) character height

  - Rate Units: Gallons/second/minute/hour/day; Liter/second/minute/hour/day; Cubic Feet/second/minute/hour/day; Cubic Meters/second/minute/hour/day; Miner’s Inch; Mega Liters/day; Million Gallons/day; Fluid Oz/second/minute/hour/day

  - Flow Totalizer: 8-digit, 0.75” (19.1mm) character height

  - Total Units: Gallon, Gallon x 1,000, Liters, Mega Liter, Cubic Meter, Acre feet, Acre Inch, Cubic feet, Cubic Feet x 1,000, Million Gallon, Miner’s Inch, Fluid Ounce

  - Pulse output Range: 0.1 – 99999.9 units/pulse

  - Input: 5V pulse or contact closure (FT430/440) (Micro-power GMR Sensor; square wave, FT450)

  - Input Range: 2 KHx Max (FT430/440) (Micro-power GMR Sensor, square wave, FT450)

  - K-Factor Range: 0.001 – 999999.999

  - Flow Alarm Output Range: 0.1 – 99999.9

  - Password protection for tampering precention

  - Low Battery Warning (FT450): A low battery warning shall be displayed when the battery has a minimum of two weeks

- Physical

  - Housing shall be made of a 30%, fiber reinforced, polybutylene terephthalate (PBT)

  - Dimensions wall mount: 4.77” wide x 4.33” deep x 3.37” high

- Indicator Serial Number

  - The indicator serial number shall be imprinted on the flow transmitter.

- Power Requirements

  - FT430: 7-30 Vdc, 4mA

  - FT440: 7-30 Vdc, 4mA (4-20) mA when loop-powered

  - FT450: Lithium “C”, 3.6 Vdc, replaceable battery. Life expectancy ~5 years depending on usage.

- Accessories

  - 4-20 mA loop; 24-30 Vdc

  - Protective hinged cover

  - Non-resettable total

  - Built-in 120/240 Vac/12/24 Vdc dual power supply (FT430W/FT440W only)

  - Built-in 120/240 Vac/12 Vdc single power supply (FT430W only)

  - Tamper evident security seal

- Environmental

  - Indicator shall be rated NEMA 4X (IP67)

- Regulatory

  - Indicator shall be CE approved

Acceptable meters shall be Seametrics FT430/440/450 or approved equal.

LT-14357r1.0 20170727

7/27/17